## Water
NORTH PORT UTILITIES
| FIXTURE UNIT CALCULATION TABLE |  |  |  | WATER and SEWER
Date:
Customer:
Address:
Building Address:
Subdivision:
Dev. Agrmt. Name
Type of Occupancy: | Commercial | Lot # |  |  | Block: |  |  | Addition:
| Fixture Type | # Proposed |  |  | Fixture Unit Value |  |  | Fixture Units
1 | Bathroom Group (water closet, lavatory, bathtub or shower stall)
1.1 | Private | 0 |  | X | 6 |  | = | 0
1.2 | Public | 0 |  | X | 8 |  | = | 0
2 | Bathtub (with or without overhead shower)
2.1 | 1 1/2" minimum trap size | 0 |  | X | 2 |  | = | 0
2.2 | 2" trap size | 0 |  | X | 3 |  | = | 0
3 | Bidet | 0 |  | X | 3 |  | = | 0
4 | Combination Sink and Tray | 0 |  | X | 3 |  | = | 0
5 | Combination Sink and Tray with Food disposal unit | 0 |  | X | 4 |  | = | 0
6 | Dental unit with Cuspidor | 0 |  | X | 1 |  | = | 0
7 | Dental lavatory | 0 |  | X | 1 |  | = | 0
8 | Drinking Fountain | 0 |  | X | 0.5 |  | = | 0
9 | Dishwashing machine domestic | 0 |  | X | 2 |  | = | 0
10 | Floor drainage (see note #1)
10.1 | 1 1/4" | 0 |  |  | 1 |  | = | 0
10.2 | 1 1/2" | 0 |  |  | 2 |  | = | 0
10.3 | 2" | 0 |  |  | 3 |  | = | 0
10.4 | 2 1/2" | 0 |  |  | 4 |  | = | 0
10.5 | 3" | 0 |  |  | 5 |  | = | 0
10.6 | 4" | 0 |  |  | 6 |  | = | 0
11 | Kitchen Sink domestic | 0 |  | X | 2 |  | = | 0
12 | Kitchen Sink, with food waste grinder | 0 |  | X | 3 |  | = | 0
13 | Lavatory (small P.O.) 1 1/4" Minimum Trap | 0 |  | X | 1 |  | = | 0
14 | Lavatory (small P.O.) 1 1/2" Minimum Trap | 0 |  | X | 2 |  | = | 0
15 | Lavatory, Barber's beauty parlor | 0 |  | X | 2 |  | = | 0
16 | Lavatory, Surgeon's | 0 |  | X | 2 |  | = | 0
17 | Laundry tray (1 or 2 compartments) | 0 |  | X | 2 |  | = | 0
18 | Shower stall, domestic | 0 |  | X | 2 |  | = | 0
19 | Showers, (group) per head | 0 |  | X | 3 |  | = | 0
20 | Surgeon's Sinks | 0 |  | X | 3 |  | = | 0
21 | Flushing rim sink | 0 |  | X | 8 |  | = | 0
22 | service (trap standard) sink | 0 |  | X | 3 |  | = | 0
23 | service sink (P trap) | 0 |  | X | 2 |  | = | 0
24 | Pot, scullery, mop, sink, etc. | 0 |  | X | 4 |  | = | 0
25 | Urinal, pedestal, siphon jet, blowout | 0 |  | X | 8 |  | = | 0
26 | Urinal, wall lip | 0 |  | X | 4 |  | = | 0
27 | Urinal, stall, washout | 0 |  | X | 4 |  | = | 0
28 | Urinal Trough (each 2 feet section) | 0 |  | X | 2 |  | = | 0
29 | Washing Machine (residential) | 0 |  | X | 3 |  | = | 0
30 | Washing Machine (commercial) see note #1 | 0 |  | X | 0 |  | = | 0
31 | Washing sink (circular or multiple) each set of faucets | 0 |  | X | 2 |  | = | 0
32 | Water Closet, Private | 0 |  | X | 4 |  | = | 0
33 | Water Closet, Public | 0 |  | X | 6 |  | = | 0
34 | Hose Bibs | 0 |  | X | 1 |  | = | 0
| Total Number of fixture units | [6 empty] | 0 | units
Notes: | 1 Floor Drain or Trap Size | units
| 1 1/4" | 1
| 1 1/2" | 2
| 2" | 3
| 2 1/2" | 4
| 3" | 5
| 4" | 6
| Commercial washing machine | 1.5 | ERU | X | 0 |  | = | 0 | Eru
| Total Fixture Units | # | units | X | 20/170 |  | = | # | ERU's
|  | 0 |  |  | 0.11765 |  | = | 0 | ERU's
[7 empty] | + | 0 | ERU's
[8 empty] | 0 | ERU's
[6 empty] | Round to |  | 0 | ERU's
|  | 0 | ERC's | = | 0 | gpm |  | see sheet 2
|  | 0 | gpm | = | 0 | meter

## Sheet2
Instantaneous Flow Per ERU Schedule and Meter Size
Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size | Number of ERUs | Instantaneous Flow GPM | Meter Size
1 | 15 | 0.625 | 26 | 124 | 2 | 51 | 203 | 3 | 76 | 279 | 3 | 101 | 354 | 4 | 126 | 429 | 4 | 151 | 504 | 6 | 176 | 579 | 6 | 201 | 654 | 6 | 226 | 729 | 6
2 | 20 | 0.75 | 27 | 128 | 2 | 52 | 206 | 3 | 77 | 282 | 3 | 102 | 357 | 4 | 127 | 432 | 4 | 152 | 507 | 6 | 177 | 582 | 6 | 202 | 657 | 6 | 227 | 732 | 6
3 | 25 | 0.75 | 28 | 132 | 2 | 53 | 209 | 3 | 78 | 285 | 3 | 103 | 360 | 4 | 128 | 435 | 4 | 153 | 510 | 6 | 178 | 585 | 6 | 203 | 660 | 6 | 228 | 735 | 6
4 | 30 | 1 | 29 | 136 | 2 | 54 | 212 | 3 | 79 | 288 | 3 | 104 | 363 | 4 | 129 | 438 | 4 | 154 | 513 | 6 | 179 | 588 | 6 | 204 | 663 | 6 | 229 | 738 | 6
5 | 35 | 1 | 30 | 140 | 2 | 55 | 215 | 3 | 80 | 291 | 3 | 105 | 366 | 4 | 130 | 441 | 4 | 155 | 516 | 6 | 180 | 591 | 6 | 205 | 666 | 6 | 230 | 741 | 6
6 | 40 | 1 | 31 | 143 | 2 | 56 | 218 | 3 | 81 | 294 | 3 | 106 | 369 | 4 | 131 | 444 | 4 | 156 | 519 | 6 | 181 | 594 | 6 | 206 | 669 | 6 | 231 | 744 | 6
7 | 45 | 1 | 32 | 146 | 2 | 57 | 221 | 3 | 82 | 297 | 3 | 107 | 372 | 4 | 132 | 447 | 4 | 157 | 522 | 6 | 182 | 597 | 6 | 207 | 672 | 6 | 232 | 747 | 6
8 | 50 | 1.5 | 33 | 149 | 2 | 58 | 224 | 3 | 83 | 300 | 3 | 108 | 375 | 4 | 133 | 450 | 4 | 158 | 525 | 6 | 183 | 600 | 6 | 208 | 675 | 6 | 233 | 750 | 6
9 | 55 | 1.5 | 34 | 152 | 2 | 59 | 227 | 3 | 84 | 303 | 3 | 109 | 378 | 4 | 134 | 453 | 4 | 159 | 528 | 6 | 184 | 603 | 6 | 209 | 678 | 6 | 234 | 753 | 6
10 | 60 | 1.5 | 35 | 155 | 2 | 60 | 230 | 3 | 85 | 306 | 3 | 110 | 381 | 4 | 135 | 456 | 4 | 160 | 531 | 6 | 185 | 606 | 6 | 210 | 681 | 6 | 235 | 756 | 6
11 | 64 | 1.5 | 36 | 158 | 2 | 61 | 233 | 3 | 86 | 309 | 3 | 111 | 384 | 4 | 136 | 459 | 4 | 161 | 534 | 6 | 186 | 609 | 6 | 211 | 684 | 6 | 236 | 759 | 6
12 | 68 | 1.5 | 37 | 161 | 3 | 62 | 237 | 3 | 87 | 312 | 3 | 112 | 387 | 4 | 137 | 462 | 4 | 162 | 537 | 6 | 187 | 612 | 6 | 212 | 687 | 6 | 237 | 762 | 6
13 | 72 | 1.5 | 38 | 164 | 3 | 63 | 240 | 3 | 88 | 315 | 3 | 113 | 390 | 4 | 138 | 465 | 4 | 163 | 540 | 6 | 188 | 615 | 6 | 213 | 690 | 6 | 238 | 765 | 6
14 | 76 | 1.5 | 39 | 167 | 3 | 64 | 243 | 3 | 89 | 318 | 3 | 114 | 393 | 4 | 139 | 468 | 4 | 164 | 543 | 6 | 189 | 618 | 6 | 214 | 693 | 6 | 239 | 768 | 6
15 | 80 | 1.5 | 40 | 170 | 3 | 65 | 246 | 3 | 90 | 321 | 4 | 115 | 396 | 4 | 140 | 471 | 4 | 165 | 546 | 6 | 190 | 621 | 6 | 215 | 696 | 6 | 240 | 771 | 6
16 | 84 | 1.5 | 41 | 173 | 3 | 66 | 249 | 3 | 91 | 324 | 4 | 116 | 399 | 4 | 141 | 474 | 4 | 166 | 549 | 6 | 191 | 624 | 6 | 216 | 699 | 6 | 241 | 774 | 6
17 | 88 | 1.5 | 42 | 176 | 3 | 67 | 252 | 3 | 92 | 327 | 4 | 117 | 402 | 4 | 142 | 477 | 4 | 167 | 552 | 6 | 192 | 627 | 6 | 217 | 702 | 6 | 242 | 777 | 6
18 | 92 | 1.5 | 43 | 179 | 3 | 68 | 255 | 3 | 93 | 330 | 4 | 118 | 405 | 4 | 143 | 480 | 4 | 168 | 555 | 6 | 193 | 630 | 6 | 218 | 705 | 6 | 243 | 780 | 6
19 | 96 | 1.5 | 44 | 182 | 3 | 69 | 258 | 3 | 94 | 333 | 4 | 119 | 408 | 4 | 144 | 483 | 4 | 169 | 558 | 6 | 194 | 633 | 6 | 219 | 708 | 6 | 244 | 783 | 6
20 | 100 | 2 | 45 | 185 | 3 | 70 | 261 | 3 | 95 | 336 | 4 | 120 | 411 | 4 | 145 | 486 | 4 | 170 | 561 | 6 | 195 | 636 | 6 | 220 | 711 | 6 | 245 | 786 | 6
21 | 104 | 2 | 46 | 188 | 3 | 71 | 264 | 3 | 96 | 339 | 4 | 121 | 414 | 4 | 146 | 489 | 4 | 171 | 564 | 6 | 196 | 639 | 6 | 221 | 714 | 6 | 246 | 789 | 6
22 | 108 | 2 | 47 | 191 | 3 | 72 | 267 | 3 | 97 | 342 | 4 | 122 | 417 | 4 | 147 | 492 | 4 | 172 | 567 | 6 | 197 | 642 | 6 | 222 | 717 | 6 | 247 | 792 | 6
23 | 112 | 2 | 48 | 194 | 3 | 73 | 270 | 3 | 98 | 345 | 4 | 123 | 420 | 4 | 148 | 495 | 4 | 173 | 570 | 6 | 198 | 645 | 6 | 223 | 720 | 6 | 248 | 795 | 6
24 | 116 | 2 | 49 | 197 | 3 | 74 | 273 | 3 | 99 | 348 | 4 | 124 | 423 | 4 | 149 | 498 | 4 | 174 | 573 | 6 | 199 | 648 | 6 | 224 | 723 | 6 | 249 | 798 | 6
25 | 120 | 2 | 50 | 200 | 3 | 75 | 276 | 3 | 100 | 351 | 4 | 125 | 426 | 4 | 150 | 501 | 6 | 175 | 576 | 6 | 200 | 651 | 6 | 225 | 726 | 6 | 250 | 801 | 6
Meter Sizing (AWWA Std)
| Flow | Positive Displacement | Compound | Turbine
| 0 | 0.625 | n/a | n/a
| 19 | 0.625 | n/a | n/a
| 20 | 0.75 | n/a | n/a
| 29 | 0.75 | n/a | n/a
| 30 | 1 | n/a | n/a
| 49 | 1 | n/a | n/a
| 50 | 1.5 | n/a | n/a
| 99 | 1.5 | n/a | n/a
| 100 | 2 | 2 | 2
| 159 | 2 | 2 | 2
| 160 | n/a | 3 | 3
| 319 | n/a | 3 | 3
| 320 | n/a | 4 | 3
| 349 | n/a | 4 | 3
| 350 | n/a | 4 | 4
| 499 | n/a | 4 | 4
| 500 | n/a | 6 | 4
| 559 | n/a | 6 | 4
| 560 | n/a | 6 | 6
| 999 | n/a | 6 | 6
| 1000 | n/a | 6X8 | 6
| 1399 | n/a | 6X8 | 6
| 1400 | n/a | 6X8 | 8
| 1599 | n/a | 6X8 | 8
| 1600 | n/a | n/a | 8
| 2000 | n/a | n/a | 8
| 2399 | n/a | n/a | 8
| 2400 | n/a | n/a | 10
| 3800 | n/a | n/a | 10